ArborGate G1

AM-G1 · Quick-Start & Wiring Guide

Setup Steps

1.  Mount & power: Install the IP67 enclosure at the gateway site (pump house, orchard hub, or field cabinet). Connect plug-in power, or deploy on solar / onboard battery for sites without a power port.

2.  Attach antennas: Connect the external SMA antennas for field radio (LPWAN), cellular, and GNSS before powering on.

3.  Join the site network: Choose the uplink path, Wi-Fi, Ethernet, or cellular LTE, and configure DHCP or static IP, the same way an IP camera joins a site network.

4.  Register in A.I.M: Open the A.I.M Hardware tab and add the gateway by Type UUID, Scan QR, or Scan barcode.

5.  Wire the pump / VFD: Connect RS485 Modbus to the VFD or compatible pump controller. Use the on-board relay if the gateway will switch or enable VFD supply directly.

6.  Verify status: Confirm join and pump link on the OLED status display, then check schedules, alerts, and field monitoring from A.I.M Web or Mobile.

7.  Push updates: Once online, the gateway accepts OTA firmware updates from A.I.M, no site visit required for future updates.

Wiring Reference

| Terminal / Interface | Function |
| --- | --- |
| Pump / VFD link | RS485 Modbus terminal pair, connect to VFD or compatible pump controller |
| VFD supply relay | On-board relay output to switch / enable VFD supply on command |
| Auxiliary power | 5V and GND terminals for accessory power |
| Expansion terminal group | Multi-signal block for accessory / sensor wiring |
| Electrical sensing | Multi-channel voltage (0–24V class) and current (0–20mA class) inputs |
| Digital I/O | Configurable digital channels with status indication |
| Host port | USB 5V host for supported peripherals |
| Data card | Removable memory card slot for offline logging |
| Antennas | External SMA connectors, field radio, cellular, GNSS |

Power Options

| Power Mode | Notes |
| --- | --- |
| Plug-in supply | Standard powered installation with charging / power-assist |
| Solar panel | 12–24V input, 40–60W panel class, MPPT-based charge management, supports solar-only sites with no power port |
| Onboard battery | 4S LiFePO4, 6500mAh, up to 96 hours of backup if power is shut down (site load and temperature dependent) |

Before You Power On

- Confirm enclosure gaskets and cable glands are seated, IP67 rating depends on a fully closed case.

- Match VFD / pump controller Modbus settings (address, baud rate) to the gateway configuration before enabling the relay.

- For solar-only sites, allow the battery to reach a healthy charge before disconnecting external power.

- Keep the removable memory card installed for offline logging continuity if cloud connectivity drops.